TECHNICAL REQUIREMENTS AND SPECIFICATIONS

REHABILITATION OF CONCRETE AND MASONRY

MANHOLES OR UNDERGROUND VAULTS

WITH A PROTECTIVE COATING

- GENERAL

  - SUMMARY

    - This specification covers all labor, materials, equipment and services necessary to complete the manhole rehabilitation work as herein specified.

    - Related Sections:  Environmental, Health and Safety

  - REFERENCES

    - ASTM D638 - Tensile Properties of Plastics.

    - ASTM D790 - Flexural Properties of Unreinforced and Reinforced Plastics.

    - ASTM D695 - Compressive Properties of Rigid Plastics.

    - ASTM D4541 - Pull-off Strength of Coatings Using a Portable Adhesion Tester.

    - ASTM D2584 - Volatile Matter Content.

    - ASTM D543 - Resistance of Plastics to Chemical Reagents.

    - ASTM C109 - Compressive Strength Hydraulic Cement Mortars.

    - ACI 506.2-77 - Specifications for Materials, Proportioning, and Application of Shotcrete.

    - ASTM C579 - Compressive Strength of Chemically Setting Silicate and Silica Chemical Resistant Mortars.

    - SSPC SP-13/NACE No. 6 – Surface Preparation of Concrete

    - ASTM - The published standards of the American Society for Testing and Materials, West Conshohocken, PA.

    - NACE - The published standards of National Association of Corrosion Engineers (NACE International), Houston, TX.

    - SSPC - The published standards of the Society of Protective Coatings, Pittsburgh, PA.

    - Los Angeles County Sanitation District – Evaluation of Protective Coatings for Concrete.

    - SSPWC 210-2.3.3 - Chemical resistance testing published in the Standard Specifications for  Public Works Construction (otherwise known as “The Greenbook”).

  - SUBMITTALS

    - Product Data:

      - Technical data sheet on each product used.

      - Material Safety Data Sheet (MSDS) for each product used.

      - Copies of independent testing performed on the coating product indicating the product meets the requirements as specified herein.

      - Technical data sheet and project specific data for repair materials to be topcoated with the coating product(s) including application, cure time and surface preparation procedures.

    - Contractor Data:

      - Current documentation from coating product manufacturer certifying Contractor’s training and equipment complies with the Quality Assurance requirements specified herein.

      - Five (5) recent references of Contractor indicating successful application of coating product(s) of the same material type as specified herein, applied by spray application within the municipal wastewater environment.

  - QUALITY ASSURANCE

    - Coating product(s) shall be capable of being installed and curing properly within a manhole environment.  Coating product(s) shall be resistant to all forms of chemical or bacteriological attack found in municipal sanitary sewer systems; and, capable of adhering to the manhole structure substrates.

    - Repair product(s) shall be fully compatible with coating product(s) including ability to bond effectively forming a composite system.

    - Contractor shall utilize equipment for the spray application of the coating product(s) which has been approved by the coating product manufacturer; and, Contractor shall have received training on the operation and maintenance of said equipment from the coating product manufacturer.

    - Contractor shall be trained by, or have their training approved and certified by, the coating product manufacturer for the handling, mixing, application and inspection of the coating product(s) to be used as specified herein.

    - Inspectors shall be trained in the use of testing or inspection instrumentation and knowledgeable of the proper use, preparation and installation of the coating product(s) to be used as specified herein.

    - Contractor shall initiate and enforce quality control procedures consistent with the coating product(s) manufacturer recommendations and applicable NACE or SSPC standards as referenced herein.

    - Pre-construction meeting shall take place no less than two weeks prior to Contractor mobilization.  All parties to have physical presence on the project during construction shall be present.  At this meeting responsibilities and authorities during construction shall be discerned; comments and questions regarding materials and execution of these specifications shall be presented and addressed.

  - DELIVERY, STORAGE, AND HANDLING

    - Materials are to be kept dry, protected from weather and stored under cover.

    - Protective coating materials are to be stored between 50 deg F and 90 deg F.   Do not store near flame, heat or strong oxidants.

    - Protective coating materials are to be handled according to their material safety data sheets.

  - SITE CONDITIONS

    - Contractor shall conform with all local, state and federal regulations including those set forth by OSHA, RCRA and the EPA and any other applicable authorities.

    - Confined space entry, flow diversion and/or bypass plans shall be presented by Contractor as necessary to perform the specified work.

  - SPECIAL WARRANTY

    - Contractor shall warrant all work against defects in materials and workmanship for a period of one (1) year, unless otherwise noted, from the date of final acceptance of the project.  Contractor shall, within a reasonable time after receipt of written notice thereof, repair defects in materials or workmanship which may develop during said one (1) year period, and any damage to other work caused by such defects or the repairing of same, at his own expense and without cost to the Owner.

- PRODUCTS

  - EXISTING PRODUCTS

    - Standard Portland cement or new concrete (not quick setting high strength cement) must cured a minimum of 28 days prior to application of the coating product(s).

    - Remove existing coatings prior to application of the coating product(s) which may affect the performance and adhesion of the coating product(s).

    - Thoroughly clean and prepare existing products to effect a seal with the coating product(s).

  - REPAIR AND RESURFACING PRODUCTS

    - Repair products shall be used to fill voids, bugholes, and/or smooth transitions between components prior to the installation of the coating product(s).  Repair materials must be compatible with the specified coating product(s) and shall be used and applied in accordance with the manufacturer’s recommendations.

    - Resurfacing products shall be used to fill large voids, lost mortar in masonry structures, smooth deteriorated surfaces and rebuild severely deteriorated structures.

    - The following products may be accepted and approved as compatible repair and resurfacing products for use within the specifications:

      - 100% solids, solvent-free epoxy grout specifically formulated for epoxy topcoating compatibility.

      - Factory blended, rapid setting, high early strength, fiber reinforced, non-shrink repair mortar that can be trowelled or pneumatically spray applied may be approved if specifically formulated to be suitable for topcoating with the specified coating product(s).

  - COATING PRODUCTS

    - Manufacturer:  Raven Lining Systems, Broken Arrow, Oklahoma  800-324-2810, 918-615-0020 or FAX 918-615-0140.

    - Product:  Raven 405 – 100% solids, solvent-free ultra high-build epoxy system exhibiting the following characteristics:

      - Product Type:  amine cured epoxy

      - VOC Content (ASTM D2584):  0%

      - Compressive Strength, psi (ASTM D695):  18,000 (minimum)

      - Tensile Strength, psi (ASTM D638):  7,500 (minimum)

      - Flexural Modulus, psi (ASTM D790):  600,000 (minimum)

      - Adhesion to Concrete, mode of failure (ASTM D4541):  Substrate (concrete) failure

      - Chemical Resistance (ASTM D543/G20) all types of service for:

        - Municipal sanitary sewer environment

        - Sulfuric acid, 30%

        - Sodium hydroxide, 5%

      - Successful Pass: Sanitation District of L.A. County Coating Evaulation Study or SSPWC 210.2.3.3 (Greenbook “Pickle Jar” Chemical Resistance test)

  - COATING APPLICATION EQUIPMENT

    - Manufacturer approved heated plural component spray equipment.

    - Hard to reach areas, primer application and touch-up may be performed using hand tools.

- EXECUTION

  - EXAMINATION

    - Appropriate actions shall be taken by Contractor to comply with local, state and federal regulatory and other applicable agencies with regard to environment, health and safety during work.

    - All structures to be coated shall be readily accessible to Contractor.

    - New Portland cement concrete structures shall have endured a minimum of 28 days since manufacture prior to commencing coating installation.

    - Any active flows shall be dammed, plugged or diverted as required to ensure all liquids are maintained below or away from the surfaces to be coated.

    - Temperature of the surface to be coated should be maintained between 40 and 120 deg F.

    - Specified surfaces should be shielded to avoid exposure of direct sunlight or other intense heat source.  Where varying surface temperatures do exist, coating installation should be scheduled when the temperature is falling versus rising.

    - Prior to commencing surface preparation, Contractor shall inspect all surfaces specified to receive the coating and notify Owner, in writing, of any noticeable disparity in the site, structure or surfaces which may interfere with the work, use of materials or procedures as specified herein.

  - SURFACE PREPARATION

    - Oils, grease, incompatible existing coatings, waxes, form release, curing compounds, efflorescence, sealers, salts, or other contaminants which may affect the performance and adhesion of the coating to the substrate shall be removed.

    - Concrete and/or mortar damaged by corrosion, chemical attack or other means of degradation shall be removed so that only sound substrate remains.

    - Choice of surface preparation method(s) should be based upon the condition of the structure and concrete or masonry surface, potential contaminants present, access to perform work, and required cleanliness and profile of the prepared surface to receive the coating product(s).

    - Surface preparation method, or combination of methods, that may be used include high pressure water cleaning, high pressure water jetting, abrasive blasting, shotblasting, grinding, scarifying, detergent water cleaning, hot water blasting and others as described in NACE No. 6/SSPC SP-13.  Whichever method(s) are used, they shall be performed in a manner that provides a uniform, sound clean neutralized surface suitable for the specified coating product(s).

    - Infiltration shall be stopped by using a material which is compatible with the repair products and is suitable for topcoating with the coating product(s).

[If severe infiltration is identified during assessment, specifications should include additional details for required methods such as chemical grouting.]

    - Manhole Chimney Joint and Casting:  The area between the manhole and the manhole ring and the manhole casting shall be a termination point of the specified coating product(s).

[If chimney seals are desired, specifications should be expanded to include these materials and their installation.]

  - APPLICATION OF REPAIR AND RESURFACING PRODUCTS

    - Areas where rebar has been exposed shall be repaired in accordance with the Project Engineer’s recommendations.

[Optional insertion if rebar is known to be exposed, and replacement not required.]  Areas where rebar has been exposed and is corroded shall be first prepared in accordance with Section 3.2.  The exposed rebar shall then be abrasive blasted and coated with coating product specified.

    - Repair products shall be used to fill voids, bugholes, and other surface defects which may affect the performance or adhesion of the coating product(s).

    - Resurfacing products shall be used to repair, smooth or rebuild surfaces with rough profiles to provide a concrete or masonry substrate suitable for the coating product(s) to be applied.  These products shall be installed to minimum thickness as recommended within manufacturers published guidelines.  Should structural rebuild be necessary, these products shall be installed to a thickness as specified by the Project Engineer.

[Note:  Structural rebuild should be specified in advance of bid whenever feasible, change orders may otherwise result.]

    - Repair and resurfacing products shall be handled, mixed, installed and cured in accordance with manufacturer guidelines.

    - All repaired or resurfaced surfaces shall be inspected for cleanliness and suitability to receive the coating product(s).  Additional surface preparation may be required prior to coating application.

  - APPLICATION OF COATING PRODUCT(S)

    - Application procedures shall conform to the recommendations of the coating product(s) manufacturer, including environmental controls, product handling, mixing, application equipment and methods.

    - Spray equipment shall be specifically designed to accurately ratio and apply the coating product(s) and shall be in proper working order.

    - Contractors qualified in accordance with Section 1.4 of these specifications shall perform all aspects of coating product(s) installation.

    - Prepared surfaces shall be coated by spray application of the coating product(s) described herein to a minimum wet film thickness of 125 mils.

[Coating thickness recommendations are available through the coating product manufacturer based upon project assessment.  Contact the manufacturer for project specific recommendations.]

    - Subsequent topcoating or additional coats of the coating product(s) shall occur within the product’s recoat window.  Additional surface preparation procedures will be required if this recoat window is exceeded.

    - Coating product(s) shall interface with adjoining construction materials throughout the manhole structure to effectively seal and protect concrete or masonry substrates from infiltration and attack by corrosive elements.  Procedures and materials necessary to effect this interface shall be as recommended by the coating product(s) manufacturer.

    - Termination points of the coating product(s) shall be made at the manhole chimney joint, 1” below normal flow levels at the bench or within the invert [unless invert is specified to receive coating], and a minimum of 1” interfacing with each pipe penetration.

    - [Optional]  Sewage flow shall be stopped, bypassed or diverted for application of the coating product(s) to the invert and interface with pipe materials.

  - TESTING AND INSPECTION

    - During application a wet film thickness gauge, meeting ASTM D4414 - Standard Practice for Measurement of Wet Film Thickness of Organic Coatings by Notched Gages, shall be used.  Measurements shall be taken, documented and attested to by Contractor for submission to Owner.

    - [Optional – Holiday Detection is recommended for coating systems installed in corrosive environments, when it can be safely and effectively performed.  Structure size and active flowing liquids may restrict the use of holiday detection.]  After the coating product(s) have set in accordance with manufacturer instructions, all surfaces shall be inspected for holidays with high-voltage holiday detection equipment.  Reference NACE RPO 188-99 for performing holiday detection.  All detected holidays shall be marked and repaired by abrading the coating surface with grit disk paper or other hand tooling method.  After abrading and cleaning, additional coating can be hand applied to the repair area.  All touch-up/repair procedures shall follow the coating manufacturer's recommendations.  Documentation on areas tested, results and repairs made shall be provided to Owner by Contractor.

    - [Optional – Adhesion Testing is a destructive test method and should be used in moderation as an evaluation tool.]  A minimum of 10% of the manholes coated shall be tested for adhesion/bond of the coating to the substrate.  Testing shall be conducted in accordance with ASTM D4541 as modified herein.  Owner’s representative shall select the manholes to be tested.  A minimum of three 20 mm dollies shall be affixed to the coated surface at the cone area, mid section and at the bottom of the structure.  The adhesive used to attach the dollies to the coating shall be rapid setting with tensile strengths in excess of the coating product and permitted to cure in accordance with manufacturer recommendations.  The coating and dollies shall be adequately prepared to receive the adhesive.  Failure of the dolly adhesive shall be deemed a non-test and require retesting.  Prior to performing the pull test, the coating shall be scored to within 30 mils of the substrate by mechanical means without disturbing the dolly or bond within the test area.  Two of the three adhesion pulls shall exceed 200 psi or concrete failure with more than 50% of the subsurface adhered to the coating.  Should a structure fail to achieve two successful pulls as described above, additional testing shall be performed at the discretion of the Owner or Project Engineer.  Any areas detected to have inadequate bond strength shall be evaluated by the Project Engineer.  Further bond tests may be performed in that area to determine the extent of potentially deficient bonded area and repairs shall be made by Contractor.

    - Visual inspection shall be made by the Project Engineer and/or Inspector.  Any deficiencies in the finished coating shall be marked and repaired according to the procedures set forth herein by Contractor.

    - The municipal sewer system may be returned to full operational service as soon as the final inspection has taken place.

END OF SECTION